Centrifugal Fan Operation

MET Fluid Mechanics Lab

FAN Equations:

- V = [ (2/ρ) (P]1/2

- Qm = VA2 for inlet manometer flow measurement; Qhwa = Vhwa A1

- Power = Q(P

- (h = (P/ρg

- g: gravitational constant

- A1: pipe area, m2

- A2: orifice area, m2.  The diameter of the orifice is 4-inches.

Part 1: Calculate flow rate from orifice meter; compare flow rate calculated from inlet manometer to the flow rate determined by HWA  values.

- Power ON for transformer and Trainer modules.

- Fan regulator ON.

- Outlet damper wide open.

- Check inlet manometer level.

- Inlet damper wide open.

- Measure the inlet pipe ID.

- Set Fan speed to get (P = 0.9 in.W.C. ; adjust RPM to decrease (P from 0.9in WG to about 0.1inWG.

- YOU MUST MAINTAIN POSITIVE CONTROL OF DAMPERS TO ELIMINATE DRIFTING.

- Measure the air velocity at the fan inlet damper with the hot wire anemometer at each damper setting.

- Complete the table below

|  | Fan Speed (rpm) | Inlet Manometer (inWC) | H.W.A. (fpm) | Outlet (P (inWC) | Fan Power (Watts) |
| --- | --- | --- | --- | --- | --- |
| 1. |  |  |  |  |  |
| 2. |  |  |  |  |  |
| 3. |  |  |  |  |  |
| 4. |  |  |  |  |  |
| 5. |  |  |  |  |  |
| 6. |  |  |  |  |  |

Complete Table for Data Section:

| Fan Speed (rpm) | Inlet Pressure (Pa) | Inlet Q (m3/s) | Outlet Pressure (Pa) | HWA (m3/s) | Calculated Fan Power (W) | Fan Efficiency (%) |
| --- | --- | --- | --- | --- | --- | --- |

- Calculate the power added to the air stream.

- Compare with power used. Calculate efficiency ( = calculated power / measured power as a %.

Report:

- Plot these results:

  - Inlet (P vs Qm.

  - Qhwa vs Manometer Qm.

  - Power into air vs. Qm

  - Efficiency vs Qm.

2. Comment on the performance trends shown in each plot.